## READ ME
|  | Language | English
Solar Powered Cold & Freezing Rooms with Monoblocs Design Toolbox
Introduction
This tool calculates the required solar system for a cold/freezing room run by monoblocs. Exemplary data is filled and can be modified by own data
Tips & Tricks
Enter values into coloured cells only! None entry cells are protected.
Overview of the following sheets
| 1. Geographic Data |  |  | For selecting basic site information: ambient temperature and solar radiation
| 2. Input |  |  | For adding data about the product to be cooled under given conditions
| 3.Technical Design Output |  |  | System configuration based on your inputs
| 4. Cost |  |  | An estimated cost of the system
| 5.Weather Data |  |  | For adding weather data of your own location if not already there
| 5. Weather Data |  |  | To add weather data for a specific location
| Calculation Sheet (Hidden) |  |  | All calculations are done within this sheet
| Translation sheet (Hidden) |  |  | Contains the translation into several languages
This tool was created by Solar Cooling Engineering
In cooperation with
© Solar Cooling Engineering GmbH, Germany - 2024
www.solar-cooling-engineering.com

## 1 Geographic Data
1. Geographic Data
Choose location:
Kenya (Kisumu)
| January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 25 | 26 | 26 | 26 | 25 | 23 | 22 | 23 | 24 | 25 | 25 | 25
Solar irradiation [kWh/m² day]: | 6.8116 | 7.0782 | 6.7087 | 6.2323 | 5.6677 | 5.6333 | 5.58 | 6.3668 | 6.093 | 6.5184 | 6.261 | 6.709
Use to obtain indicative monthly irradiation and temperature data for the site: |  |  |  | https://re.jrc.ec.europa.eu/pvg_tools/en/
Locations can be added on the sheet "Weather Data"

## 2 Input
Product information
Total mass to be cooled | Mass = | 500 | kg/day
Moisture content of the product | MC = | 86 | % wet based
or Heat capacity of the product | cp = | 0 | kJ/kg K
Radius | r = | 0.035 | m
Density | δ = | 997 | kg/m³
Convection air - product | h = | 5 | W/m²K
Temperature information
|  |  |  | Initial temperature of the product |  | Ti = | 25 | °C
|  |  |  | Cold/Freezing Room Set Point |  | Tm = | 4 | °C
|  |  |  | Refrigeration Unit |  |  | Watts
|  |  |  | Rated Electrical Power |  |  | 1000
Cold Room |  | m3
|  | 31.74 | m3
Inner length of the cold room (m) | x = | 2.3 | m
Inner width of the cold room (m) | y = | 6 | m
Inner height of the cold room (m) | z = | 2.3 | m
Thermal Conductivity of Insulation W m−1 K−1 | k / l = | 0.04 | W/m K
Thickness of Insulation (m) | L = | 0.1 | m
Ice storage inside the cold room? |  | No |  |  | Refrigeration Unit Information |  |  |  | Watts
System information
Economic information
[5 empty] | Batteries |  |  |  | Yes
Currency used for calculation |  | $ |  |  | Autonomy of the system |  |  |  | 0.5
Specific cost of PV |  | 1.1 | $/Wp |  | PV System losses (e.g. 25%) |  |  |  | 30 | %
PV lifetime |  | 25 | years |  | Power Rating |  |  |  | 480 | 0
Specif cost of battery |  | 2.5 | $/Ah@12V
Battery lifetime |  | 5 | years
Cost of a Monoblock cooling unit |  | 2500 | $
Solar cooling unit lifetime |  | 15 | years
Costs of aditional materials (cold cell, waterchiller box, pipes, water pump) |  | 8000 | $
Maintenance costs per year |  | 200 | $
Additional income per product unit |  | 0 | $/kg or l
Additional income per month |  | 500 | $/month
Discount rate |  | 5 | %
Inflation |  | 3 | %
Solar System
|  |  |  | System losses |  |  | 25 | %
|  |  |  | Autonomy days |  |  | 1 | Days

## 3 Cooling Curve (hidden)
Cooling Curve & Cooling Load

## 3 Technical Design Output
Technical Design Output
Total Cooling Demand |  | 30.7556 | kWh/day
Calculated COP |  | 2.054 | -
Cooling Power |  | 1.48 | kW
Avg Electrical Power Demand |  | 0.71747 | kW
Electricity Consumption |  | 17.2192 | kWh/day
Charging Current at 48Vdc |  | 141 | Amps
Solar PV Array |  |  | Refrigeration Units |  | Useful Battery Capacity |  | Hybrid Inverter
7.039 | kWp |  | 1 | Unit(s) | 25.83 | kWh | 3.5 | kVA

## Calculation Sheet (hidden)
Thermal losses cold month in kWh
| January | February | March | April | May | June | July | August | September | October | November | December | WORSTCASE | 0 | 0
Mean daily temperature [°C]: | 25 | 26 | 26 | 26 | 25 | 23 | 22 | 23 | 24 | 25 | 25 | 25 |  | 24 | 11.3668
Solar irradiation [kWh/m² day]: | 6.8116 | 7.0782 | 6.7087 | 6.2323 | 5.6677 | 5.6333 | 5.58 | 6.3668 | 6.093 | 6.5184 | 6.261 | 6.709 |  | Thermal losses hot month in kWh
Thermal losses for each day [kWh]: | 13.2612 | 13.8927 | 13.8927 | 13.8927 | 13.2612 | 11.9983 | 11.3668 | 11.9983 | 12.6298 | 13.2612 | 13.2612 | 13.2612 | 13.8927 | 0 | 0
Thermal Energy Liquid phase [kWh]: | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 | 11.2766 |  | 24 | 13.8927
Thermal Energy Change Phase [kWh]: | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586 | 42.9586
Thermal Energy Ice Phase [kWh]: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Max Power to cool down the product [kW]: | 0.69204 | 0.70262 | 0.70262 | 0.70262 | 0.69204 | 0.67088 | 0.6603 | 0.67088 | 0.68146 | 0.69204 | 0.69204 | 0.69204
Thermal Energy to cold down the air of the cold room once per day [kWh]: | 5.3323 | 5.5862 | 5.5862 | 5.5862 | 5.3323 | 4.8245 | 4.5706 | 4.8245 | 5.0784 | 5.3323 | 5.3323 | 5.3323
Daily Energy to cool down the product and air [kWh]: | 16.609 | 16.8629 | 16.8629 | 16.8629 | 16.609 | 16.1011 | 15.8472 | 16.1011 | 16.355 | 16.609 | 16.609 | 16.609 | 16.8629
Qtotal for each day [kW]: | 29.8702 | 30.7556 | 30.7556 | 30.7556 | 29.8702 | 28.0994 | 27.214 | 28.0994 | 28.9848 | 29.8702 | 29.8702 | 29.8702 | 30.7556
COP without battery: | 2.1017 | 2.0464 | 2.0464 | 2.0464 | 2.1017 | 2.2218 | 2.2872 | 2.2218 | 2.1601 | 2.1017 | 2.1017 | 2.1017 | 2.0464
COP : | 2.1096 | 2.054 | 2.054 | 2.054 | 2.1096 | 2.2301 | 2.2957 | 2.2301 | 2.1682 | 2.1096 | 2.1096 | 2.1096 | 2.054
Energy needed fan+pump [kWhel]: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Maximum values
Engergy needed cooling units [kWhel]: | 16.2834 | 17.2192 | 17.2192 | 17.2192 | 16.2834 | 14.4901 | 13.6325 | 14.4901 | 15.3737 | 16.2834 | 16.2834 | 16.2834 | 17.2192 |  | rounded
Cooling units needed (no battery): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1
PV Capacity fan+pump (Wp): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Cooling units needed (with battery): | 0.81417 | 0.86096 | 0.86096 | 0.86096 | 0.81417 | 0.7245 | 0.68163 | 0.7245 | 0.76868 | 0.81417 | 0.81417 | 0.81417 |  | 0.86096 | 1
PV Capacity cooling units (Wp): | 5856.8166 | 5960.1328 | 6288.407 | 6769.0694 | 7038.8469 | 6301.8945 | 5985.6105 | 5575.9277 | 6181.7757 | 6120.282 | 6371.8843 | 5946.3669 |  | 7038.8469 | 7039 | Lithium Usable (kWh) | Weco 5k3 Qty | Charging Current | Electrical Demand W | Inverter
Battery Cooling Units (Ah related to 12 V): | 4070.8538 | 4304.8058 | 4304.8058 | 4304.8058 | 4070.8538 | 3622.5176 | 3408.1333 | 3622.5176 | 3843.4244 | 4070.8538 | 4070.8538 | 4070.8538 |  | 4304.8058 | 4305 | 25830 | 5 | 140.78 | 1000 | 1
Battery Fan and Pump (Ah related to 12 V): | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Cooling Unit Run Time (hrs)
14.9732
Product information
Total mass to be cooled |  |  | Mass = | 500 | kg or l
Moisture content of the product |  |  | MC = | 86 | %
or Heat capacity of the product |  |  | cp = | 0 | kJ/kg K
Calculated heat capacity of the product: |  |  | cp = | 3.8663 | kJ/kg K
CP due to input of the user (either calculated via MC or direct) |  |  | cp = | 3.8663 | kJ/kg K
|  |  | t = | 24 | h
How many days will the product be cooled? |  |  |  | 30
Temperature information
Initial temperature of the product |  |  | Ti = | 25 | °C
Cold/Freezing Room Set Point |  |  | Tm = | 4 | °C
Cooling Unit
Cooling Power |  |  |  | 2054.0395
Power Rating |  |  |  | 1000
Number of Refrigeration Units Calculated |  |  |  | 1
Maximum Temperature within the year: |  |  | Tyearmax = | 26 | °C
Temperature within the cooling device ( Final temp - 5°C): |  |  | Tcold = | 4 | °C
Alpha - value: |  |  |  | 0.29
|  |  | COP worst case = | 3.6533
Isolation material
Inner length of the cold room |  |  | x = | 2.3 | m
Inner width of the cold room |  |  | y = | 6 | m
Inner height of the cold room |  |  | z = | 2.3 | m
Inner area of the cold room |  |  | A = | 65.78 | m²
Thermal Conductivity of Insulation W m−1 K−1 |  |  | k / l = | 0.04 | W/m K
Thickness of Insulation (m) |  |  | L = | 0.1 | m
|  |  | U = | 0.4
Cold Room Volume |  |  | V= | 31.74 | m3 | [8 empty] | Batteries:
[15 empty] | Yes | 1
[15 empty] | No | 0
System information
Ice storage inside the cold room? |  |  |  | No |  | 1
Batteries |  |  |  | Yes |  | 1
Autonomy of the system |  |  |  | 1
PV System losses (e.g. 25%) |  |  |  | 25 | %
Economic information | [6 empty] | Income
[13 empty] | Primary System + Secondary |  |  |  |  | Secondary System
Currency used for calculation |  |  |  | $
Specific cost of PV |  |  |  | 1.1 | $/Wp |  | Additional income per product: |  |  | 0 | $/year |  | Total PV Costs: |  | 7742.9 |  |  | Total PV Costs: |  |  | 0
PV lifetime |  |  |  | 25 | years |  | Additional income per year: |  |  | 6000 | $/year |  | Lifetime PV: |  | 25 |  |  | Lifetime PV: |  |  | 25
Specif cost of battery |  |  |  | 2.5 | $/Ah@12V |  | Total income : |  |  | 6000 | $/year |  | Total Battery costs: |  | 10762.5
Battery lifetime |  |  |  | 5 | years | [7 empty] | Lifetime battery: |  | 5
Cost of a Monoblock cooling unit |  |  |  | 2500 | $ | [7 empty] | Total solar cooling unit costs: |  | 2500 |  |  | Total solar cooling unit costs: |  |  | 2500
Solar cooling unit lifetime |  |  |  | 15 | years | [7 empty] | Lifetime cooling unit: |  | 15 |  |  | Lifetime cooling unit: |  |  | 15
Costs of aditional materials (cold cell, waterchiller box, pipes, water pump) |  |  |  | 8000 | $ | [7 empty] | Material & construction: |  | 8000 |  |  | Material & construction: |  |  | 8000
Maintenance costs per year |  |  |  | 200 | $/year | [7 empty] | Maintenance per year: |  | 200 |  |  | Maintenance per year: |  |  | 200
Additional income per product unit |  |  |  | 0 | $/kg or l
Additional income per month |  |  |  | 500 | $/year
Discount rate |  |  |  | 5 | %
Inflation |  |  |  | 3 | %
| Economic Analysis: System with battery |  |  |  | With batteries? |  | Yes
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
PV Costs |  | 7742.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16211.9131
Battery Costs |  | 10762.5 | 0 | 0 | 0 | 0 | 12476.6872 | 0 | 0 | 0 | 0 | 14463.9 | 0 | 0 | 0 | 0 | 16767.6243 | 0 |  | 0 | 0 | 0 | 19438.2722 | 0 | 0 | 0 | 0 | 22534.285
Solar cooling units cost |  | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3894.9185 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Material & Construction |  | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintenance costs |  | 0 | 200 | 206 | 212.18 | 218.5454 | 225.1018 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 260.9546 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 302.5179 | 311.5935 |  | 320.9413 | 330.5695 | 340.4866 | 350.7012 | 361.2222 | 372.0589 | 383.2207 | 394.7173 | 406.5588
Expenses per year: |  | 29005.4 | 200 | 206 | 212.18 | 218.5454 | 12701.789 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 14724.8547 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 20965.0608 | 311.5935 |  | 320.9413 | 330.5695 | 340.4866 | 19788.9734 | 361.2222 | 372.0589 | 383.2207 | 394.7173 | 39152.7569
Expenses per year accumulated: |  | 29005.4 | 29205.4 | 29411.4 | 29623.58 | 29842.1254 | 42543.9144 | 42775.7692 | 43014.5797 | 43260.5544 | 43513.9085 | 58238.7631 | 58507.5464 | 58784.3932 | 59069.5453 | 59363.2521 | 80328.3129 | 80639.9064 |  | 80960.8477 | 81291.4172 | 81631.9038 | 101420.8772 | 101782.0994 | 102154.1583 | 102537.379 | 102932.0963 | 142084.8532
Expenses per year accumulated (for hiding in the diagramm): |  | 29005.4 | 29205.4 | 29411.4 | 29623.58 | 29842.1254 | 42543.9144 | 42775.7692 | 43014.5797 | 43260.5544 | 43513.9085 | 58238.7631 | 58507.5464 | 58784.3932 | 59069.5453 | 59363.2521 | 80328.3129 | 80639.9064 |  | 80960.8477 | 81291.4172 | 81631.9038 | 101420.8772 | 101782.0994 | 102154.1583 | 102537.379 | 102932.0963 | 142084.8532
Accumulated income per year: |  | 0 | 6000 | 12000 | 18000 | 24000 | 30000 | 36000 | 42000 | 48000 | 54000 | 60000 | 66000 | 72000 | 78000 | 84000 | 90000 | 96000 |  | 102000 | 108000 | 114000 | 120000 | 126000 | 132000 | 138000 | 144000 | 150000
Income per year: |  |  | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 |  | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
Cashfow per year: |  | -29005.4 | 5800 | 5794 | 5787.82 | 5781.4546 | -6701.789 | 5768.1452 | 5761.1895 | 5754.0252 | 5746.646 | -8724.8547 | 5731.2167 | 5723.1532 | 5714.8478 | 5706.2933 | -14965.0608 | 5688.4065 |  | 5679.0587 | 5669.4305 | 5659.5134 | -13788.9734 | 5638.7778 | 5627.9411 | 5616.7793 | 5605.2827 | -33152.7569
Accumulated cashflow per year (for payback calculation) |  | -29005.4 | -23205.4 | -17411.4 | -11623.58 | -5842.1254 | -12543.9144 | -6775.7692 | -1014.5797 | 4739.4456 | 10486.0915 | 1761.2369 | 7492.4536 | 13215.6068 | 18930.4547 | 24636.7479 | 9671.6871 | 15360.0936 |  | 21039.1523 | 26708.5828 | 32368.0962 | 18579.1228 | 24217.9006 | 29845.8417 | 35462.621 | 41067.9037 | 7915.1468
|  | 0.55554 | 1.5713 | 2.5997 | 3.6655 | 4.3177 | 5.6493 | 6.8698 | 7.1763 | 8.3113 | 9.8562 | 10.1903 | 11.3618 | 12.4111 | 13.4345 | 14.7181 | 15.3864 | 16.422 |  | 17.4406 | 18.4521 | 19.6353 | 20.4341 | 21.448 | 22.457 | 23.4634 | 24.8384 | 26
Total initial investment costs: | 29005.4 | $
Payback period: | 7.2 | years
Net Present Value: | 6654.3978 | $
Internal Rate of Return: | 9.107%
Economic Analysis: System without battery
|  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Titles for the diagramm:
PV Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar cooling units cost |  | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3894.9185 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accumulated income
Material & Construction |  | 8000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Accumulated system costs
Maintenance costs |  | 0 | 200 | 206 | 212.18 | 218.5454 | 225.1018 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 260.9546 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 302.5179 | 311.5935 |  | 320.9413 | 330.5695 | 340.4866 | 350.7012 | 361.2222 | 372.0589 | 383.2207 | 394.7173 | 406.5588 | Accumulated system costs without batteries
Expenses per year: |  | 10500 | 200 | 206 | 212.18 | 218.5454 | 225.1018 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 260.9546 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 4197.4365 | 311.5935 |  | 320.9413 | 330.5695 | 340.4866 | 350.7012 | 361.2222 | 372.0589 | 383.2207 | 394.7173 | 406.5588
Expenses per year accumulated: |  | 10500 | 10700 | 10906 | 11118.18 | 11336.7254 | 11561.8272 | 11793.682 | 12032.4924 | 12278.4672 | 12531.8212 | 12792.7759 | 13061.5591 | 13338.4059 | 13623.5581 | 13917.2648 | 18114.7013 | 18426.2948 |  | 18747.2361 | 19077.8056 | 19418.2922 | 19768.9934 | 20130.2157 | 20502.2746 | 20885.4953 | 21280.2126 | 21686.7714
Accumulated investment per year: |  | 0 | 6000 | 12000 | 18000 | 24000 | 30000 | 36000 | 42000 | 48000 | 54000 | 60000 | 66000 | 72000 | 78000 | 84000 | 90000 | 96000 |  | 102000 | 108000 | 114000 | 120000 | 126000 | 132000 | 138000 | 144000 | 150000
Income per year: |  |  | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 |  | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000
Cashfow per year: |  | -10500 | 5800 | 5794 | 5787.82 | 5781.4546 | 5774.8982 | 5768.1452 | 5761.1895 | 5754.0252 | 5746.646 | 5739.0454 | 5731.2167 | 5723.1532 | 5714.8478 | 5706.2933 | 1802.5635 | 5688.4065 |  | 5679.0587 | 5669.4305 | 5659.5134 | 5649.2988 | 5638.7778 | 5627.9411 | 5616.7793 | 5605.2827 | 5593.4412
Accumulated cashflow per year (for payback calculation) |  | -10500 | -4700 | 1094 | 6881.82 | 12663.2746 | 18438.1728 | 24206.318 | 29967.5076 | 35721.5328 | 41468.1788 | 47207.2241 | 52938.4409 | 58661.5941 | 64376.4419 | 70082.7352 | 71885.2987 | 77573.7052 |  | 83252.7639 | 88922.1944 | 94581.7078 | 100231.0066 | 105869.7843 | 111497.7254 | 117114.5047 | 122719.7874 | 128313.2286
|  |  | 1.8112 | 2.1372 | 3.3521 | 4.4072 | 5.4324 | 6.4468 | 7.4562 | 8.4628 | 9.4676 | 10.4714 | 11.4744 | 12.4768 | 13.4788 | 14.4937 | 15.481 | 16.4823 |  | 17.4835 | 18.4846 | 19.4855 | 20.4863 | 21.4871 | 22.4877 | 23.4883 | 24.4889 | 26
Total initial investment costs: | 10500 | $
Payback period: | 1.8 | years
Net Present Value: | 59206.7829 | $
Internal Rate of Return: | 55.09%
Cooling Curve Calculation
Initial temperature of the product |  |  | Ti = | 25 | °C | [6 empty] | Time (h) | Temperature of the product
Final temperature of the product |  |  | Tm = | 4 | °C | [6 empty] | 0 | 25
[12 empty] | 1 | 14.3084
Total mass to be cooled |  |  | Mass = | 500 | kg/day | [6 empty] | 2 | 9.0601
Moisture content of the product |  |  | MC = | 86 | % wet based | [6 empty] | 3 | 6.4839
or Heat capacity of the product |  |  | cp = | 0 | kJ/kg K |  | Calculated heat Capacity of the product: |  |  | 3.8663 | kJ/kg K | 4 | 5.2193
Radius |  |  | r = | 0.035 | m |  | cp value due to selection: |  |  | 3.8663 | kJ/kg K | 5 | 4.5985
Density |  |  | δ = | 997 | kg/m³ | [6 empty] | 6 | 4.2938
Convection air - product |  |  | h = | 5 | W/m²K | [6 empty] | 7 | 4.1442
[12 empty] | 8 | 4.0708
[12 empty] | 9 | 4.0348
Volumen Product | 0.00010102 | m³ | [9 empty] | 10 | 4.0171
Surface Product | 0.015394 | m² | [9 empty] | 11 | 4.0084
Time constant Tau | 5059.2688 | s | [9 empty] | 12 | 4.0041
Product Mass | 100.7188 | g/unit | [9 empty] | 13 | 4.002
Cold Room Volume | 31.74 | m3 |  |  |  |  | T: Temperature Cooling medium |  |  |  |  | 14 | 4.001
[7 empty] | Tset: Start temperature |  |  |  |  | 15 | 4.0005 |  | Titles for the diagramm
[7 empty] | t: Time (s) |  |  |  |  | 16 | 4.0002
[12 empty] | 17 | 4.0001 |  | Cooling Curve
Cooling Load Calculation | [11 empty] | 18 | 4.0001 |  | Temperature in °C
[12 empty] | 19 | 4 |  | Time in h
[12 empty] | 20 | 4 |  | Temperature of the product
Total mass to be cooled |  |  | Mass = | 500 | kg/day | [6 empty] | 21 | 4
Area of the refrigerator |  |  | A = | 65.78 | m² | [6 empty] | 22 | 4
Thermal conductivity of insulation |  |  | k / l = | 0.04 | W/m K | [6 empty] | 23 | 4
Thickness of insulation |  |  | L = | 0.1 | m | [6 empty] | 24 | 4
Ice storage inside the cold room? |  |  |  | No
Final temperature of the product |  |  | Tm = | 4 | °C
U | 0.4 | W/m²
cp value due to selection: | 3.8663 | kJ/kg
| Time (h) | T product (°C) | T Ambient (°C) | Q Product (kW) | Q transmission (losses through insulation) (kW) | Accumulated Cooling load in kWh
| 0 | 25 | 26.6 | 5.7412 | 0.59465 | 0
| 1 | 14.3084 | 27.3 | 2.8182 | 0.61307 | 6.3359
| 2 | 9.0601 | 28 | 1.3834 | 0.63149 | 9.7672
| 3 | 6.4839 | 28.6 | 0.67907 | 0.64728 | 11.782
| 4 | 5.2193 | 27.7 | 0.33334 | 0.62359 | 13.1084
| 5 | 4.5985 | 26.8 | 0.16363 | 0.59991 | 14.0653
| 6 | 4.2938 | 25.8 | 0.080321 | 0.5736 | 14.8289
| 7 | 4.1442 | 24.3 | 0.039428 | 0.53413 | 15.4828
| 8 | 4.0708 | 23 | 0.019354 | 0.49993 | 16.0564
| 9 | 4.0348 | 21.8 | 0.0095004 | 0.46835 | 16.5756
| 10 | 4.0171 | 21.3 | 0.0046635 | 0.4552 | 17.0535
| 11 | 4.0084 | 20.9 | 0.0022892 | 0.44467 | 17.5134
| 12 | 4.0041 | 20.4 | 0.0011237 | 0.43152 | 17.9603
| 13 | 4.002 | 20.1 | 0.00055161 | 0.42362 | 18.393
| 14 | 4.001 | 19.7 | 0.00027077 | 0.4131 | 18.8171
| 15 | 4.0005 | 19.3 | 0.00013291 | 0.40257 | 19.2305
| 16 | 4.0002 | 19.1 | 6.5244e-05 | 0.39731 | 19.6332
| 17 | 4.0001 | 18.8 | 3.2027e-05 | 0.38942 | 20.0306 |  |  |  | Titles for the diagramm
| 18 | 4.0001 | 18.6 | 1.5721e-05 | 0.38416 | 20.42 |  |  |  | Time in h
| 19 | 4 | 19.5 | 7.7171e-06 | 0.40784 | 20.8042 |  |  |  | Accumulated Cooling load in kWh
| 20 | 4 | 21 | 3.7881e-06 | 0.4473 | 21.212 |  |  |  | Cooling load
| 21 | 4 | 22.5 | 1.8595e-06 | 0.48677 | 21.6594
| 22 | 4 | 24 | 9.1279e-07 | 0.52624 | 22.1461
| 23 | 4 | 25.3 | 4.4806e-07 | 0.56045 | 22.6724
| 24 | 4 | 26.6 |  | 0.59465 | 23.2328
| 5.17 | 6.01 | 6.19 | 6.28 | 6.02 | 5.57 | 5.14 | 4.97 | 5.3 | 5.56 | 5.53 | 5.26
| 5.17 | 6.01 | 6.19 | 6.28 | 6.02 | 5.57 | 5.14 | 4.97 | 5.3 | 5.56 | 5.53 | 5.26

## 4 Cost
Technical Design Output |  |  | Specific Cost |  |  | Total Cost
PV Size | 7.039 | kWp | PV installed cost | 550 | $/kWp | PV | 3871.45
Battery Size (Useful Energy) | 25.83 | kWh | Battery installed cost | 400 | $/kWh | Battery | 10332
Inverter Size | 3.5 | kVA | Inverter installed cost | 900 | $/kVA | Inverter | 3150
Cold Room Total Area | 65.78 | m² | Cold Room installed cost | 110 | $/m² | Cold Room | 7235.8
Refrigeration Units | 1 |  | Refrigeration Unit | 2200 | $/unit | Refrigeration Units | 2200
[6 empty] | Other Cost | 2000
[6 empty] | Total | 28789.25

## 5 Weather Data
Selection: Kenya (Kisumu) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 25 | 26 | 26 | 26 | 25 | 23 | 22 | 23 | 24 | 25 | 25 | 25
Solar irradiation [kWh/m² day]: | 6.8116 | 7.0782 | 6.7087 | 6.2323 | 5.6677 | 5.6333 | 5.58 | 6.3668 | 6.093 | 6.5184 | 6.261 | 6.709
[13 empty] | Selection: | Kenya (Kisumu)
Kenya (Kisumu) | January | February | March | April | May | June | July | August | September | October | November | December | List of locations:
Mean daily temperature [°C]: | 25 | 26 | 26 | 26 | 25 | 23 | 22 | 23 | 24 | 25 | 25 | 25 |  | Kenya (Kisumu)
Solar irradiation [kWh/m² monthly]: | 211.16 | 198.19 | 207.97 | 186.97 | 175.7 | 169 | 172.98 | 197.37 | 182.79 | 202.07 | 187.83 | 207.98
Solar irradiation [kWh/m² day]: | 6.8116 | 7.0782 | 6.7087 | 6.2323 | 5.6677 | 5.6333 | 5.58 | 6.3668 | 6.093 | 6.5184 | 6.261 | 6.709 |  | Mali (Bamako)
Benin (Porto Novo)
Mali (Bamako) | January | February | March | April | May | June | July | August | September | October | November | December |  | Kigali (Rwanda)
Mean daily temperature [°C]: | 25.1 | 27.8 | 30.3 | 31.1 | 31.5 | 29 | 27.4 | 25.9 | 26.4 | 27.4 | 26.5 | 24.8 |  | Ilorin (Nigeria)
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 5.4 | 5.9 | 6.9 | 6.6 | 6.4 | 6.1 | 5.8 | 5.6 | 5.8 | 5.8 | 5.7 | 5.4 |  | Lagos (Nigeria)
Mogadischu (Somalia)
Benin (Porto Novo) | January | February | March | April | May | June | July | August | September | October | November | December |  | Tamale,Ghana
Mean daily temperature [°C]: | 28 | 29 | 29.5 | 29 | 28 | 27 | 26 | 26 | 26.5 | 27 | 28 | 28.5 |  | Accra,Ghana
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 5.929 | 5.9286 | 5.7097 | 5.8 | 5.0839 | 4.0167 | 4.1355 | 4.429 | 4.4067 | 4.5323 | 5.2567 | 5.7065 |  | +++ Add location +++
Kigali (Rwanda) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 21.1 | 20.6 | 20.3 | 19.9 | 20 | 20.2 | 20.9 | 21.8 | 20.8 | 19.9 | 19.3 | 18.9
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 4.7856 | 5.2885 | 5.503 | 4.5672 | 5.2656 | 4.917 | 5.4128 | 5.8016 | 5.4282 | 4.6341 | 4.8777 | 5.3544
Ilorin (Nigeria) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 27.2 | 28.5 | 29.4 | 29.2 | 27.8 | 25.9 | 24.2 | 24.4 | 24.1 | 25.5 | 27.4 | 26.9
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 6.1935 | 6.4667 | 6.1913 | 6.3467 | 5.7 | 5.0733 | 4.3789 | 4.5133 | 4.4129 | 5.7661 | 6.2 | 6.0323
Lagos (Nigeria) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 27.9 | 28.2 | 28.2 | 27.8 | 26.6 | 25.6 | 24.9 | 24.7 | 25.3 | 26.3 | 27.3 | 26.6
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 5.9935 | 5.54 | 6 | 5.6267 | 5.2623 | 3.9667 | 3.9355 | 5.3 | 4.9545 | 5.3667 | 5.5065 | 5.629
Mogadischu (Somalia) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 27 | 26.3 | 27.2 | 28.2 | 27.2 | 25.9 | 24.7 | 24.6 | 25.5 | 26 | 26.3 | 25.7
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 6.9355 | 6.7667 | 7.2258 | 6.7 | 5.9355 | 5.9 | 5.7097 | 6.6 | 6.6774 | 6.8333 | 6.5 | 6.7097
Tamale,Ghana | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 29.1 | 30 | 32.6 | 31.9 | 30.7 | 28.3 | 25.8 | 26.1 | 25.6 | 26.9 | 28.4 | 27.8
Solar irradiation [kWh/m² monthly]: | 194.05 | 196.61 | 200.37 | 192.27 | 195.74 | 163.19 | 156.18 | 159.66 | 146.33 | 184.81 | 186.09 | 188.35
Solar irradiation [kWh/m² day]: | 6.2597 | 7.0218 | 6.4635 | 6.409 | 6.3142 | 5.4397 | 5.0381 | 5.1503 | 4.8777 | 5.9616 | 6.203 | 6.0758
Accra,Ghana | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 24.5 | 25.8 | 23.7 | 24 | 22.1 | 22.4 | 22.6 | 22.5 | 23.5 | 23.2 | 23.6 | 24
Solar irradiation [kWh/m² monthly]: | 211.16 | 198.19 | 207.97 | 186.97 | 175.7 | 169 | 172.98 | 197.37 | 182.79 | 202.07 | 187.83 | 207.98
Solar irradiation [kWh/m² day]: | 6.8116 | 7.0782 | 6.7087 | 6.2323 | 5.6677 | 5.6333 | 5.58 | 6.3668 | 6.093 | 6.5184 | 6.261 | 6.709
+++ Add location +++ | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]:
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]:

## Translation (hidden)
Selected language: | English
Number: | 1
|  | 1 | 2 | 3 | 4
Appearence in the tool |  | English | Français | Español | Deutsch
Solar Powered Cold & Freezing Rooms with Monoblocs Design Toolbox | Read me | Solar Powered Cold & Freezing Rooms with Monoblocs Design Toolbox | Chambres froides et de congélation solaires avec monoblocs Boîte à outils de conception
Read Me Sheet |  | Read Me Sheet | Lisez-moi
Introduction |  | Introduction | Introduction
This tool calculates the required solar system for a cold/freezing room run by monoblocs. Exemplary data is filled and can be modified by own data |  | This tool calculates the required solar system for a cold/freezing room run by monoblocs. Exemplary data is filled and can be modified by own data | Cet outil calcule le système solaire nécessaire pour une chambre froide/congélation fonctionnant avec des monoblocs. Des données exemplaires sont fournies et peuvent être modifiées par des données propres.
Tips & Tricks |  | Tips & Tricks | Conseils et astuces
Enter values into coloured cells only! None entry cells are protected. |  | Enter values into coloured cells only! None entry cells are protected. | Saisissez des valeurs uniquement dans les cellules colorées! Les cellules qui ne doivent pas être remplies sont protégées.
Overview of the following sheets |  | Overview of the following sheets | Aperçu des feuilles
1. Geographic Data |  | 1. Geographic Data | 1. Geographic Data | 1. Geographic Data | 1. Geographic Data
2. Input |  | 2. Input | 2. Input | 2. Input | 2. Input
3. Cooling Curve |  | 3. Cooling Curve | 3. Cooling Curve | 3. Cooling Curve | 3. Cooling Curve
4. Output |  | 4. Output | 4. Output | 4. Output | 4. Output
5. Weather Data |  | 5. Weather Data | 5. Weather Data | 5. Weather Data | 5. Weather Data
Calculation Sheet (Hidden) |  | Calculation Sheet (Hidden) | Feuille de calcul (caché)
Translation sheet (Hidden) |  | Translation sheet (Hidden) | Feuille de traduction (caché)
For selecting basic site information: ambient temperatures or solar radiation. |  | For selecting basic site information: ambient temperatures or solar radiation. | Pour choisir des informations de base sur le site: températures ambiantes ou rayonnement solaire. | Selection de datos climaticos: Temperatura ambiente y radiación solar
For adding data about the product to be cooled under given conditions |  | For adding data about the product to be cooled under given conditions | Pour ajouter des données sur le produit à refroidir dans des conditions données
Visualization of the Cooling Curve and Cooling Load profile |  | Visualization of the Cooling Curve and Cooling Load profile | Visualisation de la courbe de refroidissement et du profil de charge de refroidissement
For an overview of the results |  | For an overview of the results | Pour un aperçu des résultats
To add weather data for a specific location |  | To add weather data for a specific location | Pour ajouter des données météorologiques pour un endroit spécifique | Para añadir datos meteorológicos para una ubicación específica
All calculations are done within this sheet |  | All calculations are done within this sheet | Tous les calculs sont effectués dans cette feuille
Contains the translation into several languages |  | Contains the translation into several languages | Contient la traduction en plusieurs langues
Additional information |  | Additional information | Informatios supplémentaires
This tool was created by Solar Cooling Engineering |  | This tool was created by Solar Cooling Engineering | Cet outil a été créé par le groupe de Solar Cooling Engineering
In cooperation with |  | In cooperation with | En coopération avec
1. Geographic Data | 1 Geographic Data | 1. Geographic Data | 1. Données géographiques
Mean daily temperature [°C]: |  | Mean daily temperature [°C]: | Temperature quotidienne moyenne [°C]
Solar irradiation [kWh/m² day]: |  | Solar irradiation [kWh/m² day]: | Irradiation solaire [kWh/m² jour]
January |  | January | Janvier
February |  | February | Février
March |  | March | Mars
April |  | April | Avril
May |  | May | Mai
June |  | June | Juin
July |  | July | Juillet
August |  | August | Août
September |  | September | Septembre
October |  | October | Octobre
November |  | November | Novembre
December |  | December | Décembre
Locations can be added on the sheet "Weather Data" |  | Locations can be added on the sheet "Weather Data" | Des localisations peuvent être ajoutées sur la feuille "Weather Data" | Las ubicaciones pueden ser añadidas en la hoja "Weather Data".
Choose location: |  | Choose location: | Selectionner localisation: | Selectionar ubicación:
Use to obtain indicative monthly irradiation and temperature data for the site: |  | Use to obtain indicative monthly irradiation and temperature data for the site: | À utiliser pour obtenir des données indicatives mensuelles sur l’irradiation et la température du site:
Input of parameters | 2 Input | Input of parameters | Entrée de paramètres
Product information |  | Product information | Information du produit
Data |  | Data | Données
Total mass to be cooled |  | Total mass to be cooled | Masse totale à refroidir
Moisture content of the product |  | Moisture content of the product | Teneur en humidité du produit
or Heat capacity of the product |  | or Heat capacity of the product | ou capacité thermique du produit
Mass = |  | Mass = | Masse =
MC = |  | MC = | MC =
cp = |  | cp = | cp =
kg or l |  | kg or l | kg ou l
% wet based |  | % wet based | % à base humide
kJ/kg K |  | kJ/kg K | kJ/kg K
Radius |  | Radius | Rayon
Density |  | Density | Densité
Convection air - product |  | Convection air - product | Convection air - produit
Conduction coefficient of the product |  | Conduction coefficient of the product | Coefficient de conduction du porduit
Temperature information |  | Temperature information | Information des températures
Initial temperature of the product |  | Initial temperature of the product | Température initiale du produit
Freezing Room Temperature Set-Point |  | Freezing Room Temperature Set-Point | Température finale du produit
Time to cool down the product |  | Time to cool down the product | Temps pour refroidir le produit
How often do you cool down the product |  | How often do you cool down the product | À quelle fréquence refroidissez-vous le produit?
per month |  | per month | par mois
System information |  | System information | Informations du système
Batteries |  | Batteries | Batteries
Autonomy of the system |  | Autonomy of the system | Autonomie du système
PV System losses (e.g. 25%) |  | PV System losses (e.g. 25%) | Pertes du système
PV Panels |  | PV Panels | Panneau solaires
Charge Controller |  | Charge Controller | Contrôleur de charge
Batteries |  | Batteries | Batteries
Control Unit |  | Control Unit | Unité de control
Compressor |  | Compressor | Compressseur
Ice storage |  | Ice storage | Stockage de glace
Water bath |  | Water bath | Bain d'eau
Ice on evaporator surface |  | Ice on evaporator surface | Glace surface de l'évaporateur
DC pump |  | DC pump | Pompe CC
Fan coil unit |  | Fan coil unit | Ventilo-convecteur
Cold room |  | Cold room | Chambre froide
Cooled product |  | Cooled product | Produit refroidi
Yes |  | Yes | Oui
No |  | No | Non
Cold Room |  | Cold Room | Chambre froide
Inner length of the cold room |  | Inner length of the cold room | Longueur intérieur de la chambre froide
Inner width of the cold room |  | Inner width of the cold room | Largeur intérieur de la chambre froide
Inner height of the cold room |  | Inner height of the cold room | Hauteur intérieur de la chambre froide
Area of the cold room |  | Area of the cold room | Surface du réfrigérateur
Thermal conductivity of insulation |  | Thermal conductivity of insulation | Conductivité thermique de l'isolation
Thickness of insulation |  | Thickness of insulation | Épaisseur de l'isolation
Ice storage inside the cold room? |  | Ice storage inside the cold room? | Stockage de glace dans la chambre froide?
Economic information |  | Economic information | Informations économiques
Currency used for calculation |  | Currency used for calculation | Devise utilisée pour le calcul
Specific cost of PV |  | Specific cost of PV | Coût spécifique du PV
PV lifetime |  | PV lifetime | PV durée de vie
Specif cost of battery |  | Specif cost of battery | Coût spécifique de la batterie
Battery lifetime |  | Battery lifetime | Durée de vie de la batterie
Cost of a Monoblock cooling unit |  | Cost of a Monoblock cooling unit | Coût d'une unité de refroidissement Monoblock
Solar cooling unit lifetime |  | Solar cooling unit lifetime | Durée de vie de l'unité de refroidissement solaire
Costs of aditional materials (cold cell, waterchiller box, pipes, water pump) |  | Costs of aditional materials (cold cell, waterchiller box, pipes, water pump) | Coûts de matériel et de construction pour la glacière
Maintenance costs per year |  | Maintenance costs per year | Coûts de maintenance par an
years |  | years | années
Additional income per product unit |  | Additional income per product unit | Revenu supplémentaire par unité de produit
Additional income per month |  | Additional income per month | Revenu supplémentaire par mois
Discount rate |  | Discount rate | Taux de remise
Inflation |  | Inflation | Inflation
$/kg or l |  | $/kg or l | $/kg ou l
$/Wp |  | $/Wp | $/Wc
$/month |  | $/month | $/mois
Cooling Curve | 3 Cooling Curve | Cooling Curve | Courbe de refroidissement
Temperature in °C |  | Temperature in °C | Température en °C
Time in h |  | Time in h | Temps en h
Temperature of the product |  | Temperature of the product | Température du produit
Accumulated Cooling load in kWh |  | Accumulated Cooling load in kWh | Charge de refroidissement accumulée en kWh
Cooling load |  | Cooling load | Charge de refroidissement
Thermal losses cold month in kWh |  | Thermal losses cold month in kWh | Pertes thermiques mois froid en kWh
Thermal losses hot month in kWh |  | Thermal losses hot month in kWh | Pertes thermiques mois chaud en kWh
Cooling Curve & Cooling Load |  | Cooling Curve & Cooling Load | Courbe de refroidissement et charge de refroidissement
0
Results | 4 Output | Results | Résultats
System Design (Secondary System) |  | System Design (Secondary System) | Conception du système sans batteries
Monoblock Cooling units needed: |  | Monoblock Cooling units needed: | Unités de refroidissement monobloc nécessaires :
Cooling units costs: |  | Cooling units costs: | Coûts des unités de refroidissement:
Solar PV size: |  | Solar PV size: | Taille PV solaire:
Solar PV costs: |  | Solar PV costs: | Coûts PV solaire:
Battery size: |  | Battery size: | Taille des batteries:
Battery costs: |  | Battery costs: | Coûts des batteries:
Total initial investment: |  | Total initial investment: | Investissement initial total:
Payback period: |  | Payback period: | Période de récupération:
Net present value: |  | Net present value: | Valeur actuelle nette:
Internal rate of return: |  | Internal rate of return: | Taux de rendement interne:
System Design |  | System Design | Conception du système avec batteries
years |  | years | années
Accumulated income & system costs over 20 years |  | Accumulated income & system costs over 20 years | Revenu accumulé et coûts du système sur 20 ans
Years |  | Years | Années
Accumulated income |  | Accumulated income | Revenu accumulé
Accumulated system costs without batteries |  | Accumulated system costs without batteries | Coûts accumulé du système sans batteries
Accumulated system costs |  | Accumulated system costs | Coûts accumulé du système avec batteries